## Slide 1: Grid integration of rooftop solar: An economic loss/gain to discom?
Akanksha Tyagi, Neeraj Kuldeep, Selna Saji
Energy Horizons 2019
New Delhi
18 July 2019
© Council on Energy, Environment and Water, 2019 and BSES Rajdhani Power Limited (BRPL)
Session Partner

## Slide 2: CEEW – Among South Asia’s leading policy research institutions
Energy Access
Renewables
Low-Carbon Pathways
Technology, Finance, & Trade
Industrial Sustainability & Competitiveness
Risks & Adaptation
Power Sector
Centre for Energy Finance

## Slide 3: Agenda
Introduction (5 min)
Methodology (20 min)
Case study (15 min)
Tool demonstration (30 min)

## Slide 4: Introduction

## Slide 5: Introduction
India’s rooftop solar sector
40 GW national target for rooftop solar by 2022
3.8 GW installed capacity of rooftop solar as of FY191
1. CEEW compilation from multiple sources: MNRE, Bridge to India, Mercom
Chart: Annual trends in rooftop solar capacity additions in India
| FY12 | FY13 | FY14 | FY15 | FY16 | FY18 | FY19
Annual capacity additions | 38 | 79 | 169 | 337 | 520 | 1188 | 1513
Cumulative capacity | 38 | 117 | 286 | 623 | 1143 | 2331 | 3844
Maharashtra
Rajasthan
Tamil Nadu
Gujarat
Karnataka

## Slide 6: Introduction
Challenges
Opportunities
Discom: Distribution companies; T&D losses : transmission and distribution losses; RPO: renewable purchase obligation
Revenue loss
Inadequate technical staff
Infrastructure upgradation
Inequitable billing methods
Need for improved solar valuation methods
Rooftop solar and discoms
Demand management
RPO targets
Network decongestion
Reduction in T&D losses
Notes: Inequitable billing methods: gross, net, virtual: volumetric and Uniform feed-in tariff (location, time not imp): loss to discom: peak or non-peak ; loading of DT
Infra: dt cap, grid balancing, intermittent nature of solar
Lack of incentives: Transmission charges are exempted

## Slide 7: Introduction
Value of grid-connected rooftop solar (VGRS)
Cost-benefit analysis method
Location and time specific
Equitable compensation of solar electricity
Flexibility to choose different perspectives: discom, consumer, society
Notes: Uniform feed-in tariff (location, time not imp): loss to discom: peak or non-peak ;
loading of DT

## Slide 8: Introduction
Relevance of VGRS to discom
Efficient demand and supply management
Wiser investments for grid upgradation
Strategic deployment of rooftop solar projects
Support for equitable solar tariffs and operational incentives
Notes: Uniform feed-in tariff (location, time not imp): loss to discom: peak or non-peak ;
loading of DT

## Slide 9: Methodology

## Slide 10: VGRS methodology
Identify benefits and costs of rooftop solar to discom
Define framework
Estimate net benefit and cost
Case study and tool demonstration

## Slide 11: Costs and benefits of rooftop solar to discoms
Revenue loss
Program administration cost
Added transmission and distribution services cost
Costs
Generation
Avoided generation capacity cost (AGCC)
Avoided power purchase cost (APPC)
Transmission
Avoided transmission charges
Distribution
Avoided distribution capacity infrastructure and related O&M cost
Externalities
Avoided renewable energy certificate cost
Reduced working capital
Benefits

## Slide 12: Costs of rooftop solar to discom
Migration of consumers from grid to rooftop solar
Reduction in DISCOM’s receivables
Variable tariff and load profile of each consumer category
Rooftop solar data: number and capacity of rooftop solar, solar generation profile
Data requirement
  Revenue loss

## Slide 13: Costs of rooftop solar to discom
Additional network component required to evacuate and manage rooftop solar
Expenses to install and maintain new network components
Constraint: Depends on when new components will be added
Cost of procuring and maintaining new network components
Rooftop solar data: number and capacity of rooftop solar
Data requirement
  Added transmission and distribution services cost

## Slide 14: Costs of rooftop solar to discom
Technical staff recruitment, site visits, panel cleaning
Additional expenses to discom
Salary of additional technical staff recruited for rooftop solar
Cost of all programs specific to rooftop solar
Data requirement
Program administration cost

## Slide 15
Are there additional cost parameter?

## Slide 16: Benefits of rooftop solar to discom
Benefit
Rooftop solar
System
(generation/ transmission/ distribution)
General formula of evaluating benefit

## Slide 17: Benefits of rooftop solar to discom
Reduced generation capacity requirement
Savings on the fixed cost
Constraint: Depends on when power purchase agreement (PPA) with genco is due
Genco: generation company
Avoided generation capacity cost (AGCC)
Cost of the procured capacity from the genco
Load profile
Transmission loss (TL)
Rooftop solar data: number and capacity of rooftop solar, solar generation profile
Data requirement

## Slide 18: Benefits of rooftop solar to discom
Reduced power requirement
Savings on the variable cost
Constraint: none
Avoided power purchase cost (APPC)
Variable component of power purchase cost (open access and merit order)
Transmission and distribution losses (TL, DL)
Rooftop solar data: number and capacity of rooftop solar
Data requirement

## Slide 19: Benefits of rooftop solar to discom
Reduced transmission capacity requirement
Savings on the transmission charges
Constraint: Depends on when power purchase agreement (PPA) with TRANSCO is due
Transco: transmission company
Avoided transmission charges (ATRC)
Transmission charges payable to the transco
Load profile
Transmission and distribution losses (TL, DL)
Rooftop solar data: number and capacity of rooftop solar, solar generation profile
Data requirement

## Slide 20: Benefits of rooftop solar to discom
Delayed distribution transformer (DT) upgradation
Savings on upgradation and maintenance
Constraint: Depends on when DT upgradation is due
O&M: operation and maintenance
DT load profile
Cost to install, operate and maintain the new DT
Transmission and distribution losses (TL, DL)
Rooftop solar data: number and capacity of rooftop solar, solar generation profile
Data requirement
  Avoided distribution capacity infrastructure and related O&M cost (ADCC)

## Slide 21: Benefits of rooftop solar to discom
Available solar generation enough to meet renewable purchase obligation (RPO) targets
Savings on renewable energy certificates (RECs)
Constraint: Depends on the validity of RECs in future
Cost of RECs
Rooftop solar data: number and capacity of rooftop solar, solar generation profile
Data requirement
  Avoided renewable energy certificate cost

## Slide 22
Are there additional benefit parameters?

## Slide 23: Costs and benefits of rooftop solar to discoms
Revenue loss
Program administration cost
Added transmission and distribution services cost
Costs
Generation
Avoided generation capacity cost (AGCC)
Avoided power purchase cost (APPC)
Transmission
Avoided transmission charges
Distribution
Avoided distribution capacity infrastructure and related O&M cost
Externalities
Avoided renewable energy certificate cost
Reduced working capital
Benefits
Which component contributes most?

## Slide 24: Challenges in VGRS
Comprehension
Multiple components
Data availability
Granular data required
Data accuracy
Long term projections
Computation limitations
Scaling up the analysis from DT level to the entire service area
Feedback

## Slide 25: Case study

## Slide 26: Selection of distribution transformers
Rated Capacity
100 kVA
Peak Loading
Low
High
RTS penetration
Low (<10 per cent)
High (>10 per cent)
Consumer category
Residential
Industrial
Commercial
Government
Institutional
630 kVA
990 kVA

## Slide 27: Selection of distribution transformers
 | DT 1 | DT 2 |  | DT 3 | DT 4 | DT 5 | DT 6 | DT 7 | DT 8
DT capacity (kVA) | 100 | 630 |  | 990 | 100 | 100 | 990 | 990 | 990
Total RTS capacity considered (kW) | 35 | 220 |  | 102 | 10 | 80 | 10 | 30 | 63.3
Individual RTS capacities (kW) | 35 | 20 | 200 | 102 | 10 | 80 | 10 | 30 | 63.3
Consumer category | Industrial | Commercial | Government | Commercial | Residential | Institutional | Residential | Government | Institutional
DCF | 27.09% | 36.14% | 33.57% | 7.38% | 19.10% | 37.25% | 14.86% | 20.10% | 5.51%

## Slide 28: Contribution of rooftop solar in peak reduction at DT level
Chart: Percecntage
| DT 1 | DT 2 | DT 3 | DT 4 | DT 5 | DT 6 | DT 7 | DT 8
Solar Capacity (kW) | 35 | 220 | 102 | 10 | 80 | 10 | 30 | 63.3
CUF | 0.1134 | 0.11914 | 0.1166 | 0.1351 | 0.1032 | 0.1168 | 0.139 | 0.1288
SCF | 0.1331 | 0.13795 | 0.1243 | 0.1492 | 0.1151 | 0.1286 | 0.1535 | 0.1259
DCF | 0.2709 | 0.33804 | 0.0738 | 0.191 | 0.3725 | 0.1486 | 0.201 | 0.0551
Solar Penetration | 0.35 | 0.35 | 0.1 | 0.1 | 0.8 | 0.01 | 0.03 | 0.06

## Slide 29: Results
Chart: 25-year discounted values per kW installed
| . DT 1 | DT 1 | . DT 2 | DT 2 | . DT 3 | DT 3 | . DT 4 | DT 4 | . DT 5 | DT 5 | . DT 6 | DT 6 | . DT 7 | DT 7 | . DT 8 | DT 8
AGCC | 8789.8 | 8924.3 | 8043.6 | 9653 | 7446.9 | 8324.7 | 9933.9 | 8149.4
APPC | 23716 | 25068 | 24609 | 28356 | 21690 | 24598 | 29277 | 26917
ATRC | 2221.9 | 2255.9 | 2033.3 | 2440.1 | 1882.5 | 2104.4 | 2511.2 | 2060.1
ADCC | 5633.5 | 120.88 | 0 | 0 | 0 | 0 | 0 | 0
ARECC | 11224 | 11793 | 11539 | 13374 | 10218 | 11565 | 13761 | 12753
AWCC | 391.07 | 517.74 | 517.44 | 556.97 | 453.8 | 413.71 | 611.98 | 587.84
RevenueLoss | 40685 | 47173 | 46158 | 51824 | 40871 | 41926 | 55042 | 51013
CUF | 0.1134 | 0.1134 | 0.11914 | 0.11914 | 0.1166 | 0.1166 | 0.1351 | 0.1351 | 0.1032 | 0.1032 | 0.1168 | 0.1168 | 0.139 | 0.139 | 0.1288 | 0.1288
SCF | 0.1331 | 0.1331 | 0.13795 | 0.13795 | 0.1243 | 0.1243 | 0.1492 | 0.1492 | 0.1151 | 0.1151 | 0.1286 | 0.1286 | 0.1535 | 0.1535 | 0.1259 | 0.1259

## Slide 30: Net benefit from rooftop solar to discoms

## Slide 31: Utility-level scaling
ADCC has been ignored in the calculations
Chart: 
| Benefits | Revenue Loss
AGCC | 0.34376
APPC | 1.0155
ATRC | 0.086899
ARECC | 0.47979
AWCC | 0.017551
Residential | 0.21006
Commercial | 0.2165
Industrial | 0.033869
Institutional | 0.71684
Government | 0.57503

## Slide 32: Key observations and recommendations
Rooftop solar systems contribute to reducing a discom’s peak demand by about 13 per cent of its rated capacity.
Savings on power procurement and REC costs constitute about 77 per cent of the overall benefits to the discom.
Residential DTs in the BRPL area offered a maximum net gain of INR 0.86/kWh in case of high-rise societies with single point delivery of electricity.
Revenue loses in residential category is in the range of INR 1.08–1.86 for every unit of solar electricity generated compared to INR 1.74 and INR 1.92 in the industrial and commercial categories, respectively.
Discoms should promote rooftop solar systems among their subsidised consumer categories to maximise their benefits.
DTs with frequent overloading and day time peaks serve as useful targets for rooftop solar deployment to further improve the net benefit.

## Slide 33: Tool Demonstration tinyurl.com/CEEWtool

## Slide 34: Suggested values for input parameters
Parameter | Values
Annual derating | 0.5% - 0.8%
Distribution coincidence factor | 15% - 30%
Fixed capacity cost | 10,000 – 15,000
Average peak energy procurement cost | 4 – 5
Average non-peak energy procurement cost | 2 – 4
Transmission charges | 2,000 – 4,000
DT upgradation costs | 8,00,000 – 13,00,000
WACC | 13% - 17%
Debt rate | 12% - 14%

## Slide 35
Thank you
Join the conversation by using #EnergyHorizons
ceew.in | @CEEWIndia

## Slide 36: Benefits of rooftop solar to DISCOM
Available solar generation enough to meet renewable purchase obligation (RPO) targets
Savings on renewable energy certificates (RECs)
Constraint: Depends on the validity of RECs in future
TRANSCO: transmission company
Consumer categories and tariffs
Debt rate
Data requirement
  Reduced working capital

## Slide 37: Estimate net benefit and cost
Capacity procurement cost
Power Purchase cost
Projected growth rate of load
Capacity of the current DT and planned upgradation
One-time cost of upgradation of the DT
Category and consumption details (before and after solar)of consumers
Tariff escalation rate
Transmission and distribution Losses
Renewable energy certificate (REC) cost
Case study: a distribution transformer (DT) in BRPL service area
Discom data

## Slide 38: Estimate net benefit and cost
Number of rooftop solar projects planned
Rated capacity of rooftop solar
Solar generation data
Program cost
Capacity utilization factor
System coincidence factor
Case study: a distribution transformer (DT) in BRPL service area
Rooftop solar data

## Slide 39: Estimate net benefit and cost
Case study: a distribution transformer (DT) in BRPL service area
DT characteristics
CUF: 9.07%
Installed RTS capacity: 50 kW
Consumer category: Residential
SCF: 3.02%
DCF: 2.11%

## Slide 40: Assign monetary value to identified components
Use hourly data of the demand as seen by the system for the past year.
Identify the top 20% hours when the demand was the highest.
Identify RTS production during these peak hours and take their average
Divide 3 by the rating of the RTS installation to get the SystemCoincidenceFactor for that system (generation/transmission/ distribution)
Calculating the SystemCoincidenceFactor

## Slide 41: Assign monetary value to identified components
Example: SystemCoincidenceFactor for generation and transmission system
Chart: Actual Output vs Utility demand

## Slide 42: Assign monetary value to identified components
Example: SystemCoincidenceFactor for generation and transmission system
Chart: Actual Output vs Utility demand

## Slide 43: Estimate net benefit and cost
Average capacity and power procurement cost
Overall utility demand (generation and transmission) for DT level analysis
Same SystemCoincidenceFactor for generation and transmission system
Transmission cost is ratio of total transmission charges and capacity contracted
Policy on RECs remains unchanged for 25 years
Case study: a distribution transformer (DT) in BRPL service area
Assumptions

## Slide 44: Estimate net benefit and cost
Parameter | Unit | Description | Value
RTS output | kW | Rated capacity of the RTS | 35
System Coincidence Factor |  | Fraction of rated RTS output that supports the system at the latter’s peak. | 0.1434
Degradation Factor |  | Factor to account for the decrease in performance of the RTS system over the years | 0.995Y-1
Capacity Cost | INR/kW | Fixed cost of additional contracted capacity as decided by the Regulatory commission | 7452.23
TL% |  | Transmission loss per cent | 3.30%

## Slide 45: Estimate net benefit and cost
Parameter | Unit | Description | Value
RTS Energy | kWh | Electricity produced by the RTS system in the first year | 38,625
Degradation Factor |  | Factor to account for the decrease in performance of the RTS system over the years | 0.995Y-1
Var. Power Purchase Cost | INR/kWh | Variable component of the power purchase cost of the DISCOM as set by the regulatory commission | 2.81
TL% |  | Transmission loss per cent | 3.30%
DL% |  | Distribution loss per cent | 9.50%

## Slide 46: Estimate net benefit and cost
Avoided Transmission Charges
Parameter | Unit | Description | Value
RTS output | kW | Rated capacity of the RTS | 35
Trans. Coincidence Factor |  | Fraction of rated RTS output that supports the transmission system at the latter’s peak. | 0.1434
Degradation Factor |  | Factor to account for the decrease in performance of the RTS system over the years | 0.995Y-1
Transmission Cap. Cost | INR/kW | Normative transmission charges as decided by the Regulatory commission | 2970.15
TL% |  | Transmission loss per cent | 3.30%
DL% |  | Distribution loss per cent | 9.50%

## Slide 47: Estimate net benefit and cost
Avoided distribution capacity infrastructure and related O&M cost
Time deferred to upgrade DT

## Slide 48: Estimate net benefit and cost
Parameter | Unit | Description | Value
RTS output | kW | Rated capacity of the RTS | 35
Distribution Coincidence Factor |  | Fraction of rated RTS output that supports the distribution transformer at the latter’s peak. | 0.1353
Degradation Factor |  | Factor to account for the decrease in performance of the RTS system over the years | 0.995Y-1
DT Capacity | kVA | Rated capacity of the distribution transformer | 100
Peak Loading | kVA | 90th percentile DT loading in the last one year | 89.3734
Growth Rate |  | Category-wise annual growth rate mentioned in the ARR | 2.6%
Avoided distribution capacity infrastructure and related O&M cost

## Slide 49: Estimate net benefit and cost
Avoided Renewable Energy Certificate Cost
 | Unit | Description | Value
RTS Energy | kWh | Electricity produced by the RTS system in the first year | 38,625
REC Cost | INR/kWh | Cost of purchasing solar REC | 2
Derating Factor |  | Factor to account for the decrease in performance of the RTS system over the years | 0.995Y-1

## Slide 50: Estimate net benefit and cost
Reduced Working Capital
 | Unit | Description | Value
Revenue Loss | INR | Loss to the utility’s revenue due to adoption of rooftop solar by consumers | 
Avoided Costs | INR | Sum of all benefits stated prior to this | 
Debt Rate |  | The interest rate faced by the utility to finance debts | 14%

## Slide 51: Estimate net benefit and cost
Revenue loss
VariableEnergyTariff (INR/kWh): The variable energy tariff for consumers as approved by the regulatory commission
 | Unit | Description | Value
RTS Energy | kWh | Electricity produced by the RTS system in the first year | 38,625
Variable energy tariff | INR/kWh | The variable energy tariff for consumers as approved by the regulatory commission | 4.5

## Slide 52: Estimate net benefit and cost
Added transmission and distribution services cost
No data provided
Program administer cost
No data provided

## Slide 53: Net present value
Benefits (INR/kWh): |  | 
Avoided generation capacity cost | 0.20 | 
Avoided power purchase cost | 0.77 | 
Avoided transmission charges | 0.09 | 
Avoided distribution capacity cost | - | 
Avoided renewable energy certificate cost | 0.48 | 
Reduced working capital | 0.01 | 
Total Benefits | 1.54 | 
Costs (INR/kWh): |  | 
Program Administer Cost |  | -
Revenue Loss |  | 1.08
Added transmission and distribution services cost |  | -
Total Costs |  | 1.08
Net benefit/cost |  | 0.46